
SEWERAGE SECTOR GUIDANCE 
CHANGE PROPOSAL FORM
Please complete the form below to submit a change proposal to the Sewerage Adoption Panel.
	Name of Proposed Change: DCG pumping station flow rate calculations and septicity. 


	Section 1 - Proposed Change

A. Please outline the details (including any relevant supporting documentation) of the proposed change.
The inflow rates for pumping station sizing in DCG is 4000 litres per property.  We need to pump at 50% of that flow (3 x DWF), the rising main must be cleared within a 4-hour period to avoid a septic event.
With modern day, private telemetry, the fill rate into a pumping station is much less, therefore the figures for septicity calculation, inaccurate. 
Some authorities are asking for larger, oversized rising main installation therefore the retention period within the main increases.  With modern day construction, water saving initiatives which are prevalent, pumping stations and discharge mains are septic, more so that ever and water authorities will not adopt, yet the developer has done nothing wrong other than follow the guidance.  This is not a short-term operational issue. 

B. Has the proposed change been considered previously (including during any prior consultation process)? If so, please provide details.
Not to our knowledge. 

C. Does the proposed change need to be considered by a specific date?  If so, please explain why?

It is an issue now. 


D. Does the proposed change raise any health and safety issues?  If so, please provide details.
Septic sewage creates hydrogen sulphide which is deadly. 

E. Please provide any further information relevant to the change proposal.
Water authorities also do not wish to adopt chemical dosing systems, as perceived as a cost, an asset to manage.  Hydrogen sulphide rots infrastructure, so this opinion is back to front in our opinion. 


	Section 2 - Scope of the Proposed Change

A. Which section(s) of the Sewerage Sector Guidance and Model Adoption Agreement  does the proposed change concern?  Please provide specific references to the relevant documentation.

Section D5

B. What consequential amendments to the Sewerage Sector Guidance and Model Adoption Agreement would be required as a result of the proposed change? Please provide specific references.


Figures changed to reflect today.  Can you refer to water usage figures?  Water in, sewage out etc.  They must be a national monitored record of this. 


	Section 3 - Rationale for the proposed change 

A. What is the nature and effect of the current position/existing arrangements?

Frustrated adoption, house building obstructed, significant H&S risk.

B. What is the nature and effect of the proposed change?

Accurate pumping station sizing, rising main sizing and septicity reduction by association. 

C. Why is the proposed change necessary?

As above. 

D. What is the desired outcome of the proposed change?

A safer and more efficient operational environment. 


	Section 4 – Impact on the Principles and Objectives of the Code 

A. Outline, how and why the proposed change maintains consistency with the principles and objectives of the Code for Adoption Agreements, and any relevant statutory or regulatory requirements?

Whilst DCG is guidance, plus associated local practices, all pumping station providers both follow and are governed by the same.  


	Section 5 – Impact on Customers and Sewerage Companies  

A. What is the impact of the proposed change (be it positive and/or negative) on Customers?

Positive.  A reduction in septic events. Odours reduce as do hazardous by products (H2S)

B. Is there any evidence of customer concern relating to the proposed change? If so, please provide details.

We have many examples and would be happy to share. 

C. What is the impact of the proposed change (be it positive and/or negative) on Sewerage Companies?
Septic sewage reduction into the network, less odour complaints, reduced maintenance of assets due to corrosion. 

D. Estimate how much notice Customers and Sewerage Companies may reasonably require to be able to meet any new requirements arising from the proposed change.


From experience, as much as you can give them.  Nothing happens quickly. 

E. What is the suggested implementation date of the proposed change?

Now


	Section 6 – Stakeholder Engagement 

A. Please outline any informal/formal consultation undertaken with relevant stakeholders likely to be affected by the proposed change, including details of any responses provided by stakeholders.


	Section 7 – Applicant’s Details

	Name:

	Company:

	Company Registration Number:

	Company Address:

	Telephone:

	Email:
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